DENDRITE INFORMATION

in LiFePO4 batteries

Caused by lithium plating

| Parameter | Safe limit for LFP (per cell) | Why the limit matters |
| --- | --- | --- |
| Maximum charge voltage | 3.65 V ± 0.05 V (most datasheets specify 3.60 V-3.65 V) | Staying below this voltage keeps the anode potential above 0 V vs. Li/Li⁺, preventing lithium-metal plating on the graphite anode. |
| Charge rate (C-rate) | ≤ 1 C for most commercial packs (many OEMs recommend ≤ 0.5 C for longest life) | Higher currents increase local current density, which can exceed the electrolyte’s critical current density (CCD) and force plating even at normal voltage. |
| Temperature during charge | ≥ 0 °C (ideally 15 °C 35 °C) | Below 0 °C the electrolyte conductivity drops, raising the over-potential for a given current and making plating more likely. |
| Discharge cut-off | ≈ 2.5 V – 2.8 V (depends on the pack) | Discharging too deep stresses the cathode and can also increase internal resistance, indirectly affecting charge-over-potential later. |

Charge-rate control

  - Even at 3.65 V, a very high current can create a large IR drop across the cell’s internal resistance, effectively lowering the anode’s local potential enough to initiate plating.

  - Limiting to ≤ 1 C (or the manufacturer’s recommendation) keeps the current density below the electrolyte’s CCD for most standard LFP electrolytes.

- Temperature management

  - Cold temperatures increase the electrolyte’s resistance, so the same current produces a larger voltage drop, again risking a negative anode potential.

  - Keeping the pack ≥ 0 °C (preferably in the 15 °C 35 °C window) maintains low resistance and stable SEI, reducing the chance of dendrite nucleation.

## How this compares to sodium-ion (since you’re using both)

Interesting contrast:

| Feature | LFP | Sodium-ion |
| --- | --- | --- |
| Dendrite risk | Low | Very low |
| Plating tendency | Possible when cold | Much harder |
| Abuse response | Benign | Very benign |

Sodium-ion is actually even more dendrite-resistant than LFP — one of its big selling points